{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"images":4},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":104,"n_cols":5,"rows_kept":104,"merged":[[0,0,0,4],[1,0,1,4],[103,3,104,4]],"flags":["formulas_cached_only"]}
["泰州市姜城水务有限责任公司每半年度出厂水水质公示"]
["    为保证城乡居民饮用水安全，接受社会监督，现将我公司供水水质指标予以公示。此次水质公示采样日期为2025年11月11日，采样监测结果显示，我公司出厂水水质达到国家生活饮用水卫生标准GB5749-2022要求。"]
["水样类型","出厂水","采样环境","正常环境"]
["检验方式","化学检验","消毒方式","次氯酸钠"]
["序号","项目","单位","限值","检验值"]
[1,"总大肠菌群","MPN/100mL或CFU/100mL","不应检出","未检出"]
[2,"大肠埃希氏菌","MPN/100mL或CFU/100mL","不应检出","未检出"]
[3,"菌落总数","CFU/mL","≤100","未检出"]
[4,"砷","mg/L","≤0.01",0.0006]
[5,"镉","mg/L","≤0.005","<0.0001"]
[6,"铬(六价)","mg/L","≤0.05","<0.004"]
[7,"铅","mg/L","≤0.01","<0.0008"]
[8,"汞","mg/L","≤0.001",6e-05]
[9,"氰化物","mg/L","≤0.05","<0.002"]
[10,"氟化物","mg/L","≤1.0",0.22]
[11,"硝酸盐(已N计)","mg/L","＜10",{"v":1.6,"d":"1.60"}]
[12,"三氯甲烷","mg/L","≤0.06",0.009936]
[13,"一氯二溴甲烷","mg/L","≤0.1",0.002859]
[14,"二氯一溴甲烷","mg/L","≤0.06",0.004129]
[15,"三溴甲烷","mg/L","≤0.1","<0.000041"]
[16,"三卤甲烷(三氯甲烷，一氯二溴甲烷、二氯一溴甲烷，三溴甲烷的总和)",null,"≤1",0.26]
[17,"二氯乙酸","mg/L","≤0.05",0.0037]
[18,"三氯乙酸","mg/L","≤0.1","<0.0044"]
[19,"溴酸盐","mg/L","≤0.01","<0.005"]
[20,"亚氯酸盐","mg/L","≤0.7","<0.0024"]
[21,"氯酸盐","mg/L","≤0.7",0.0848]
[22,"色度(铂钴色度单位)","度","≤15","<5"]
[23,"浑浊度(散射浑浊度单位)","NTU","≤1",{"v":0.1,"d":"0.10"}]
[24,"臭和味","--","无异臭、异味","0级"]
[25,"肉眼可见物","--","无","无"]
[26,"pH","--","≥6.5并且≤8.5",7.51]
[27,"铝","mg/L","≤0.2",0.068]
[28,"铁","mg/L","≤0.3","<0.10"]
[29,"锰","mg/L","≤0.1","<0.05"]
[30,"铜","mg/L","≤1.0","<0.05"]
[31,"锌","mg/L","≤1.0","<0.02"]
[32,"氯化物","mg/L","≤250",{"v":23,"d":"23.0"}]
[33,"硫酸盐","mg/L","≤250",28.8]
[34,"溶解性总固体","mg/L","≤1000",210]
[35,"总硬度(以CaCO3计)","mg/L","≤450",136]
[36,"高锰酸盐指数(以O2计)","mg/L","≤3",1.15]
[37,"氨（以N计）","mg/L","≤0.5","<0.02"]
[38,"总α放射性","Bq/L","≤0.5","<0.02"]
[39,"总β放射性","Bq/L","≤1","<0.03"]
[40,"游离氯","mg/L","≥0.3 并且 ≤2",{"v":0.8,"d":"0.80"}]
[41,"总氯","mg/L","≥0.5并且≤3"]
[42,"臭氧","mg/L","≤0.3"]
[43,"二氧化氯","mg/L","≥0.1并且≤0.8"]
[44,"贾第鞭毛虫","个/10L","＜1",0]
[45,"隐孢子虫","个/10L","＜1",0]
[46,"锑","mg/L","≤0.005","<0.0005"]
[47,"钡","mg/L","≤0.7",0.0512]
[48,"铍","mg/L","≤0.002","<0.0001"]
[49,"硼","mg/L","≤1.0","<0.20"]
[50,"钼","mg/L","≤0.07",0.00168]
[51,"镍","mg/L","≤0.02","<0.002"]
[52,"银","mg/L","≤0.05","<0.0002"]
[53,"铊","mg/L","≤0.0001","<0.00001"]
[54,"硒","mg/L","≤0.01",0.0003]
[55,"高氯酸盐","mg/L","≤0.07",{"v":0.0062,"d":"0.00620"}]
[56,"二氯甲烷","mg/L","≤0.02","<0.0004"]
[57,"1，2-二氯乙烷","mg/L","≤0.03","<0.0004"]
[58,"四氯化碳","mg/L","≤0.002","<0.0004"]
[59,"氯乙烯","mg/L","≤0.001","<0.0004"]
[60,"1,1-二氯乙烯","mg/L","≤0.03","<0.0004"]
[61,"1，2-二氯乙烯（总量）","mg/L","≤0.05","<0.0008"]
[62,"三氯乙烯","mg/L","≤0.02","<0.004"]
[63,"四氯乙烯","mg/L","≤0.04","<0.0004"]
[64,"六氯丁二烯","mg/L","≤0.0006","<0.0004"]
[65,"苯","mg/L","≤0.01","<0.0004"]
[66,"甲苯","mg/L","≤0.7","<0.0004"]
[67,"二甲苯(总量)","mg/L","≤0.5","<0.0012"]
[68,"苯乙烯","mg/L","≤0.02","<0.0004"]
[69,"氯苯","mg/L","≤0.3","<0.0004"]
[70,"1,4-二氯苯","mg/L","≤0.3","<0.0004"]
[71,"三氯苯(总量)","mg/L","≤0.02","<0.000045"]
[72,"六氯苯","mg/L","≤0.001","<0.00025"]
[73,"七氯","mg/L","≤0.0004","<0.00034"]
[74,"马拉硫磷","mg/L","≤0.25","<0.00040"]
[75,"乐果","mg/L","≤0.006","<0.00072"]
[76,"灭草松","mg/L","≤0.3","<0.0005"]
[77,"百菌清","mg/L","≤0.01","<0.00042"]
[78,"呋喃丹","mg/L","≤0.007","<0.0005"]
[79,"毒死蜱","mg/L","≤0.03","<0.00025"]
[80,"草甘膦","mg/L","≤0.7","<0.025"]
[81,"敌敌畏","mg/L","≤0.001","<0.00042"]
[82,"莠去津","mg/L","≤0.002","<0.0005"]
[83,"溴氰菊酯","mg/L","≤0.02","<0.00101"]
[84,"2,4-滴","mg/L","≤0.03","<0.0005"]
[85,"乙草胺","mg/L","≤0.02","<0.00002"]
[86,"五氯酚","mg/L","≤0.009","<0.0005"]
[87,"2,4,6-三氯酚","mg/L","≤0.2","<0.00040"]
[88,"苯并(a)芘","mg/L","≤0.00001","<0.0000014"]
[89,"邻苯二甲酸二(2-乙基己基)酯","mg/L","≤0.008","<0.00041"]
[90,"丙烯酰胺","mg/L","≤0.0005","<0.00015"]
[91,"环氧氯丙烷","mg/L","≤0.0004","<0.00006"]
[92,"微囊藻毒素-LR","mg/L","≤0.001","<0.0002"]
[93,"钠","mg/L","≤200",19.2]
[94,"挥发酚类（以苯酚计）","mg/L","≤0.002","<0.002"]
[95,"阴离子合成洗涤剂","mg/L","≤0.3","<0.05"]
[96,"2-甲基异莰醇","mg/L","≤0.00001","<0.0000022"]
[97,"土臭素","mg/L","≤0.00001","<0.0000038"]
[]
[{"$nulls":3},"泰州市姜城水务有限责任公司\n水质检测中心"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}