{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"images":4},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":54,"n_cols":6,"rows_kept":54,"merged":[[0,0,0,5],[1,0,1,5],[52,4,52,5],[53,4,53,5]],"flags":["formulas_cached_only"]}
["泰州市姜城水务有限责任公司2026年1月份出厂水水质公示"]
["     为保证城乡居民饮用水安全，接受社会监督，现将我公司供水水质指标予以公示。此次水质公示采样日期为2026年1月5日，采样监测结果显示，我公司出厂水水质全部达到国家生活饮用水卫生标准要求。"]
["采样地点","二水厂送水泵房","水样类型","出厂水","消毒方式","次氯酸钠"]
["采样环境","正常环境","检验方式","化学检验","采样时间","2026.1.5"]
["序号","项目","单位","限值","检验值"]
[1,"总大肠菌群","MPN/100mL或CFU/100mL","不应检出","未检出"]
[2,"大肠埃希氏菌","MPN/100mL或CFU/100mL","不应检出","未检出"]
[3,"菌落总数","CFU/mL","≤100","未检出"]
[4,"砷","mg/L","≤0.01",9e-05]
[5,"镉","mg/L","≤0.005","<0.0002"]
[6,"铬(六价)","mg/L","≤0.05","<0.004"]
[7,"铅","mg/L","≤0.01","<0.0014"]
[8,"汞","mg/L","≤0.001",7e-06]
[9,"氰化物","mg/L","≤0.05","<0.002"]
[10,"氟化物","mg/L","≤1.0",0.18]
[11,"硝酸盐(已N计)","mg/L","≤10",{"v":1.8,"d":"1.80"}]
[12,"三氯甲烷","mg/L","≤0.06",0.0011]
[13,"一氯二溴甲烷","mg/L","≤0.1",0.003]
[14,"二氯一溴甲烷","mg/L","≤0.06",{"v":0.002,"d":"0.0020"}]
[15,"三溴甲烷","mg/L","≤0.1",0.0007]
[16,"三卤甲烷（三氯甲烷、一氯二溴甲烷、二氯一溴甲烷、三溴甲烷的总和）",null,"该类化合物中的各种化合物的实测浓度与其各自限值的比值之和不超过1",0.09]
[17,"二氯乙酸","mg/L","≤0.05","<0.005"]
[18,"三氯乙酸","mg/L","≤0.1","<0.008"]
[19,"溴酸盐","mg/L","≤0.01","<0.005"]
[20,"亚氯酸盐","mg/L","≤0.7","<0.004"]
[21,"氯酸盐","mg/L","≤0.7",0.051]
[22,"色度(铂钴色度单位)","度","≤15","<5"]
[23,"浑浊度(散射浑浊度单位)","NTU","≤1",{"v":0.1,"d":"0.10"}]
[24,"臭和味","级","无异臭、异味",0]
[25,"肉眼可见物","--","无","无"]
[26,"pH","--","≥6.5并且≤8.5",7.62]
[27,"铝","mg/L","≤0.2",0.088]
[28,"铁","mg/L","≤0.3","<0.05"]
[29,"锰","mg/L","≤0.1","<0.05"]
[30,"铜","mg/L","≤1.0","<0.05"]
[31,"锌","mg/L","≤1.0","<0.05"]
[32,"氯化物","mg/L","≤250",27.4]
[33,"硫酸盐","mg/L","≤250",25.2]
[34,"溶解性总固体","mg/L","≤1000",227]
[35,"总硬度(以CaCO3计)","mg/L","≤450",146]
[36,"高锰酸盐指数(以O2计)","mg/L","≤3",0.98]
[37,"氨（以N计）","mg/L","≤0.5","<0.02"]
[38,"总α放射性","Bq/L","≤0.5",0.08]
[39,"总β放射性","Bq/L","≤1",0.18]
[40,"游离氯","mg/L","≥0.3 并且 ≤2",0.6]
[41,"总氯","mg/L","≥0.5并且≤3","/"]
[42,"臭氧","mg/L",null,"/"]
[43,"二氧化氯","mg/L","≥0.1并且≤0.8","/"]
[44,"高氯酸盐","mg/L","≤0.07","<0.005"]
[45,"二氯甲烷","mg/L","≤0.02","<0.006"]
[46,"2,4,6-三氯酚","mg/L","≤0.2","<0.00005"]
[]
[{"$nulls":4},"泰州市姜城水务有限责任公司"]
[{"$nulls":4},"水质检测中心"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}